## Server room components
SL. No | Particulars | Pack Size | Quantity | Rate (NU.) | Total Amount (NU.) | Offered Specification | Manufacturer | Brand | Country of Origin | Remarks
1 | Raised Access Floor Panels for Server Room. Technical Specification: Panel Size:- 600mm x 600mm x 35mm; Point Load:- 500Kg;Uniform Load:- 2200Kg per Sq mtr; Panel Top:- HPL laminated Anti-Static; Accessories: • Complete under structure system with required accessories; • 5 mm thick floor insulation below; • Fixing of Ventilated /Perforated Tiles; • Fixing of Air Plugs under each racks; • Vaccum Pump Panel Lifter; • Providing and fixing of Ramp. Floor Height:- 60mm to 120mm adjustable | Package (Approx. 600 sqft.) | 1 | [6 empty] | Sample Required
2 | Flase Ceiling with Fire Suppression System. Technical Specification: 600 mm x 600 mm x 16 mm rectangular edge in true horizontal level suspended on locking silhouette Armstrong 15mm grid false Ceiling system with lighting facilities. Supply and installation of automatic fire suppression system with smoke and temperature detectors. The alarm notification system should be GSM based and should send SMS notice to identified mobile numbers besides email and siren. | Package (Approx. 600 sqft.) | 1 | [6 empty] | Sample Required
3 | Biometric Door Lock. Technical Specification: Fingerprint/card based door lock system | Nos | 1
4 | IP Based KVM Switch. Technical Specification:• 16-port KVM over IP switch with rackmount kits. • Should provide minimum of 1 local console and 2 remote users via TCP/IP network. • 8 nos. of PS/2 VGA adapter and 8nos. of USB VGA adapters & Virtual Media |  | 1
5 | Precision Air Conditioning. Technical Specification: • 7 Ton Air Cooled Precision ACs complete with Microprocessor based controller with RS485 & SNMP Network card, Scroll compressors, Remote air cooled Condensers with fans and drive motors, High Efficiency Filters, Heater, Humidifier, etc. • Accessories for PAC installation complete including Copper Pipes, GI pipes for drainage, Connectors, flood discharge kits, Valves, stands for Indoor and Outdoor units, power cables, nitrogen gas, Refrigerant Gas (R410A) etc. as deemed necessary. • Installation and commissioning charges including loading, unloading and shifting at site, associated civil, plumbing & electrical works, test charging with nitrogen gas, actual charging with R410a refrigerant gas, warranty and maintenance for 1 year. | Nos | 2 | [6 empty] | Please include rate for the necessary electrical works
6 | 42 U Rack for Storage of UPS. Technical Specification: 42U Equipment Rack- • 19” rack – 42U, 600mm W, 1200mm D; • DIN41494, IEC 297 and EIA 310-D compliant rack; • Top Cover & Bottom Cover With Cable Entry Provision; • Side Panel Slam Latch with Locking Facility & 1/3 perforated for ventilation; • Front fully perforated honeycomb mesh door with Lock & Key; • Rear fully perforated honeycomb double panel mesh door with Lock & Key; • Adjustable Rear Cable Management channel; • Adjustable leveling feet and castors with breaks; • 4 nos. of 230V AC 90CFM exhaust fans at top; • Front Panel Mounting Hardware. | Nos | 1
7 | PDU for Racks. Technical Specification: • 1U horizontal with rack mounting kits; • 10x IEC C13 socket with 1A MCB. | Nos | 4 | [6 empty] | Sample Required
8 | Router (VPN Capable). Technical Specification: • Minimum of 2 WAN ports, 2 LAN ports and 1 USB 3G/4G Modem Ports from day1; • Static Route, NAT, RIP and OSPF from day 1; • Minimum of 1TB SSD hard drive for content caching from day 1; • WAN Link bonding/aggregation and load balancing, bandwidth monitoring and content caching from day 1; • Required licenses and subscription for min. 3 years. | Nos | 1
9 | Unified Threat Management (UTM) Device. Technical Specification: •With firewall, application control, IPS, Anti-Virus, Anti-Bot, Anti-Spyware, URL and Content Filtering and Advanced Threat Prevention capabilities from day 1; • 8nos. of 10/100/1000 Gigabit ports and 2 nos. of SFP ports from day 1; • Minimum of 180GB SSD drive for local log storage & 12GB memory from day one; • Minimum of 25Gbps of Firewall throughput, 5.5Gbps of IPS throughput & 5.5Gbps of IPsec VPN throughput; • Required licenses and subscription for min. 3 years | Nos | 1
10 | SAN Storage. Technical Specification:• Dual Controller with 4 nos. of 16Gb/s FC ports per controller; • 8GB Cache; • 24x 300GB 15K RPM SAS HDD; • Support for RAID 1, 5 & 6; • Snapshot, Volume Copy, Remote Copy, De-duplication, Thin Provisioning | Nos | 1
11 | Servers. Technical Specification • 1U Dual Socket Rack Server; • Support up to 8x 2.5-inch Hot Plug Hard Drive; • Minimum of 24 DIMMs with memory expendable up to 1500GB; • Intel C612 Chipset; • 2x Intel Xeon E5-2620, v4, 2.10GHz, 8 Core, 20MB Cache Processor; • 2x 16GB 2Rx4 DDR4-2400 MHz ECC Memory; • 6x 450GB SAS, 12Gb/s, 15K RPM, 2.5-inch Hot Plug Hard Drive configured in RAID5 volume; • Integrated RAID Controller supporting RAID 1, 5, 6, 10 and 50 with 1GB Cache; • 1x Internal DVD-RW Super Multi Optical Drive • Integrated Remote Management Controller with 256 MB memory; • Integrated 4 port, 1Gb Network Interface Card; • 5x USB ports, 1 x VGA port; • 1x 10/100/1000 Mbit/s dedicated management LAN port for Remote Management; • 2x Modular 800W, 94% (Platinum efficiency), 100-240V, 50 / 60Hz Power Supply; • 4x Hot Plug Fan; • Rack mounting kit with cable manager; • 12 months’ hardware warranty from the date of successful delivery | Nos | 1

## Poster
SL. No | Particulars | Pack Size | Quantity | Rate (NU.) | Total Amount (NU.) | Offered Specification | Manufacturer | Brand | Country of Origin | Remarks
1 | Election Advisory Poster: Specification: Size:-45cmx65CM (BxL); Paper quality:- 250Gsm matt. Water proof Matte lamination | Piece | 1351 | [6 empty] | Sample required

## heating system
SL. No | Particulars | Pack Size | Quantity | Rate (NU.) | Total Amount (NU.) | Offered Specification | Manufacturer | Brand | Country of Origin | Remarks
Heating & Cooling System: Option 1
1 | RVariable refrigerant flow (VRF) - HVAC Heating and Air Conditioning System for Head Office of the Election Commission Building with estimated 25,000 SFT Area. The cost should include all civil works, required additional accessories and attachments. The product should come with minimum one year warranty service. The additional warranty costs should be clearly mentioned as AMC or CMC. The system should only use approved refrigerant and should be a reputed brand commonly used in Bhutan viz Blue Star, Toshiba, Samsung and equivalent brand. The power requirement if any should be clearly specified and discrepancies later during the operation shall be on bidders account. The bidder should visit ECB building prior to submission of quotation for site inspection to get the exact requirement. The bidder might be required to do the presentation on the proposal. The VRF system should be centralized system and following indoor unit: | Nos | 1 Lot | [6 empty] | Original Calatogue Required
| Hi-wall Unit/One way Cassete |  | 30
| Four-way Cassete |  | 4
| Verticools |  | 6
Heating & Cooling System: Option 2
2 | Invertor Air Conditioning System. The AC should only use approved refrigerant and should be a reputed brand commonly used in Bhutan viz Blue Star, Toshiba, Samsung and equivalent brand. The AC should have heavy duty compressor with 240v power supply. The compressor should be concealed and should not be visible. The product should come with minimum of 1 year warranty. The additional warranty costs should be clearly mentioned as AMC or CMC The indoor unit requirement are as follows: | Unit | [7 empty] | Original Calatogue Required
| Hi-wall Unit |  | 30
| Four-way Cassete |  | 4
| Verticools |  | 6